## Conversion Chart
Easy Conversion Chart: BE3-47N, 47N/27
To
ES-47N, 47N/27
This simple chart is designed to help you choose the appropriate ES style configuration with the same minimum coverage as your BE3. Just match up the color-coded option boxes on the left with those on the right. Option boxes colored black require no selection. For reference, see the product specification style charts on Page 2. For assistance, contact technical support at 618-654-2341.
Enter your BE3 style configuration below to generate new ES style configuration
From |  |  | BE3 Style Configuration |  |  |  |  | To |  |  | ES Style Configuration
BE3 | Model Number | Sensing Input Type | Nominal Input Type | Frequency | External Power | Output Type |  | ES | Model Number | Sensing Input Type | Nominal Input Type | Timing | Frequency | External Power | Option 1 | Option 2 | Option 3
| 47N | [7 empty] | 47N |  |  | B
| 47N/27 | [7 empty] | 47N/27 |  |  | B
|  | 3 | [7 empty] | 3
|  |  | A | [7 empty] | A
|  |  | B | [7 empty] | C
|  |  | C | [7 empty] | D
|  |  | D | [7 empty] | F
|  |  | S¹ | [7 empty] | S¹
|  |  |  | 2² | [8 empty] | na²
|  |  |  | 3 | [8 empty] | 1
|  |  |  | 4 | [8 empty] | 1
[5 empty] | N³ | [8 empty] | N³
2⁴
0
N
A6
0
Enter your current BE3 configuration:
BE3 |  | 3 |  |  | N | 2 |  | ES |  | 3 |  | B | 1 | N | 0 | N | 0
1 | For other nominal voltages, contact Basler Electric
2 | ES Frequency is 50/60 Hz. 400 Hz units not available.
3 | External Power is not required for ES. No selection necessary.
4 | Output Type is predefined by function for ES. No selection necessary.
5 | ES-47N, 47N/27 wiring terminals are in identical pin-out positions as previous BE3 wiring terminals. Connection diagrams are shown on Page 3 and in Instruction Manual 9500100991.
6 | Option 2 selection A not available.
Sample Style Configuration Conversion
[7 empty] | BE3-47N, 47N/27 |  | ES-47N, 47N/27
[5 empty] | Model Number, 47N |  | 47N |  | 47N | Model Number, 47N
[5 empty] | Sensing Input Type, 3P3W |  | 3 |  | 3 | Sensing Input Type, 3P3W
[5 empty] | Nominal Input Type, 120 Vac |  | A |  | A | Nominal Input Type, 120 Vac
[5 empty] | Frequency, 60 Hz |  | 4 |  | B | Timing, Adjustable, 0 to 20 seconds
[5 empty] | External Power, None |  | N |  | 1 | Frequency, 50/60 Hz
[5 empty] | Output Type, De-energize To Trip |  | 2 |  | N | External Power, Not required
[9 empty] | 0 | Option 1, None
[9 empty] | N | Option 2, None
[9 empty] | 0 | Option 3, None
Some options for the ES have been preselected in the above guide. To insure accuracy, please verify your style configuration using the ES style chart on page 2, referencing Instruction Manual 9500100991 or contacting Technical Support.
BE3-47N, BE3-47N/27 Style Number Identification Chart
ES-47N, ES-47N/27 Style Number Identification Chart
BE3-47N/27 Connection Diagram
ES-47N/27 Connection Diagram